## Input
Prepared by: | MM | Checked by: | SW
Project Number: | 2015509 | County: | PALM BEACH
Road Number:
Project Desciption: | BENOIST FARMS ROAD (SR 80/SOUTHERN BLVD TO BELVEDERE RD)
Circuit: | C-III | Date: | 2020-06-16
C-IV
Load Center Prop. Or Exist. | Existing
Load Center "C"
Load Center Sta. & Offset | STA. 116+84, 1979' LT | Service Voltage: | 480
Existing Power Source Service: | 480 V-To-Ground, 1 PHASE, 3 WIRE, 1P-280 AMP MAIN CIRCUIT BREAKER | Temp. for Wire Resistance: | 75
60 CYCLE AC RESISTANCE ONE WIRE (CU)
|  |  |  | WIRE SIZE | 25 Deg. C. | 40 Deg. C. | 75 Deg. C.
|  |  |  | (#AWG) | (OHMS/FT) | (OHMS/FT) | (OHMS/FT)
|  |  |  | 1/0 |  |  | 0.000122
|  |  |  | 8 | 0.000654 | 0.000692 | 0.000809
|  |  |  | 6 | 0.00041 | 0.0004335 | 0.00051
|  |  |  | 4 | 0.000259 | 0.000274 | 0.000321
|  |  |  | 2 | 0.000162 | 0.0001715 | 0.000201
|  |  |  | 1 | 0.0001021 | 0.00010811 | 0.000154
120/240 V, 1 PHASE, 3 WIRE, 2P-100 AMP MAIN CIRCUIT BREAKER

## Breakers
LED LIGHTING VOLTAGE DROP CALCULATIONS
| CLIENT: | PALM BEACH COUNTY
| PROJECT: | BENOIST FARMS ROAD (SR 80/SOUTHERN BLVD TO BELVEDERE RD)
| PROJECT NO: | 2015509
SERVICE TYPE: | 480 V-To-Ground, 1 PHASE, 3 WIRE, 1P-280 AMP MAIN CIRCUIT BREAKER
| Breaker Sizes | Demand Load (Amps) | Design Load (Amps) | Design (Volt Amps)
Main Breaker | 280
Branch Ckt Bkr
C-I | 40 | 21.67 | 27.0875 | 13002
C-II | 40 | 21.67 | 27.0875 | 13002
C-III | 40 | 16.58 | 20.725 | 9948
C-IV | 40 | 14.08 | 17.6 | 8448
C-V | 40 | 17.33 | 21.6625 | 10398
C-VI | 40 | 13.34 | 16.675 | 8004
Totals |  | 130.8375 | 163.5469 | 62802
Connected Load (KVA) |  | 62.802
Overcurrent Design Load (KVA) |  | 62.802

## Voltage Drop Table
EXIST. LOAD CENTER "C"
480 V-To-Ground, 1 PHASE, 3 WIRE, 1P-280 AMP MAIN CIRCUIT BREAKER
STA. 116+84, 1979' LT
LOAD CENTER AND CIRCUIT DESIGNATION | MAIN & CIRCUIT BREAKER SIZES | TOTAL CONNECTED LOAD (AMPS) | TOTAL CONNECTED LOAD (KVA)
C-I | 40 AMPS 1P (BRANCH) | 21.67 | 10.4016
C-II | 40 AMPS 1P (BRANCH) | 21.67 | 10.4016
C-III | 40 AMPS 1P (BRANCH) | 16.58 | 7.9584
C-IV | 40 AMPS 1P (BRANCH) | 14.08 | 6.7584
C-V | 40 AMPS 1P (BRANCH) | 17.33 | 8.3184
C-VI | 40 AMPS 1P (BRANCH) | 13.34 | 6.4032
| CONTINUOUS LOAD | 50241.6 | VA
| 20% SPARE CAPACITY | 10048.32 | VA
| 25% CONTINUOUS LOAD | 15072.48 | VA
| TOTAL LOAD | 75362.4 | VA
| TOTAL LOAD IN AMPS | 157.005 | A